## Sheet1
Generator Specifications | 发电机规格 | 数量 | 单价 | 总计
1250KVA (1000KW) STAND BY GENERATOR SET with soundproof construction having a sound proof metallic canopy and a high grade exhaust silencer for residential installation with the following essential parameters for the diesel engine, alternator and control panel:- | 1250 千伏安（1000 千瓦）备用发电机组，具有隔音结构、隔音金属罩和高级排气消音器，用于住宅安装，柴油发动机、交流发电机和控制面板的基本参数如下：- 柴油发动机：康明斯、道依茨、帕金斯、沃尔沃、卡特彼勒或其他型号。 | 1台
Diesel engine:- type Cummins, Deutz,Perkins, Volvo, Caterppillar or equivalent, and subject to the engineers/consultants approval. | 柴油发动机：康明斯、道依茨、帕金斯、沃尔沃、卡特彼勒或同等型号，须经工程师/顾问批准。
Speed- 1500rpm at 50HZ, with automatic speed governor | 转速--1500rpm，50HZ，带自动调速器
Lubrication- with forced oil circulation with detachable oil filter and cartridge | 润滑--强制机油循环，配有可拆卸的机油过滤器和滤芯
Cooling SYSTEM- water cooling with radiator | 冷却系统--水冷，带散热器
Electric start including batteries with cables, termination, and battery isolator switch, and battries charged by generator. | 电启动，包括带电缆、终端和电池隔离开关的电池，以及由发电机充电的电池。
Fuel tank with filter | 带过滤器的油箱
Alternator:- type Stamford, Leroy Somer, ABB, MR, MARATHON or equivalent, and subject to the engineers/consultants approval. | 交流发电机：Stamford、Leroy Somer、ABB、MR、MARATHON 或同等型号，须经工程师/顾问批准。
Three phase 1250KVA (1000KW), Y-connection and accessible neutral | 三相 1250 千伏安（1000 千瓦），Y 型连接，中性点可触及
Standard voltage : 230/400V, at 50HZ | 标准电压：230/400 伏，50 赫兹
Brushless. Windings with H class insulation | 无刷。绕组采用 H 级绝缘
Indix of protection -IP21 | 防护等级 -IP21
Electronic voltage regulator to satisfiy the voltage with in +/- 1.5% with nominal load, and power factor 0.8 lagging to unity | 电子电压调节器，满足额定负载下 +/- 1.5% 的电压要求，功率因数 0.8 滞后于统一值